2026-02-24

HMI V130 Screen seems damaged. Horizontal line 1mm-7mm from bottom & vertical 3mm band on right starting about 2mm in.

Restart in windows- not sure if unitronics does linux version

Patrickswell PS.2022 Jul.12.Dc:   chose this one ☒

Patrickswell RC1: ☐

Save as ☒                  Activate software ☒

Now Patrickswell PS.2026.26. Feb.24.Dc

Connect & get version  ☒       0/5: 4.13 (00)

V130-33-B1

Set clock ☒ ☒ Updates o/s to 4.013(28)                 Burning os ☒

Download software & set values ☒

Can’t get it into “RUN” mode maybe a problem with the program. Trying empty program. ☒ Didn’t work moved to v570 – fitted Ethernet card ☒

Trying blank program first –Errors: Pcom Password- New Cyber Security measure

Test Ethernet X

Test Canbus X

Test input  X

Test output X

Fitted Ethernet card to v570. Tried to download a program and go

Os upgrade      o/s 4.13(26) > not needed ☒

Send clock ☒

Download blank program ☒

Stop reason no Pcom password ☒

V130 maybe the same ☒

Ethernet Pcom Password – needs to be configured

Understand how this works ☒

Password: - P4tr1ck5    9 charts     This may be hard to type out

Hex 2D 50 34 74 31 63 6B 35